SPECIFICATIONS – accessories: Discharge relief valve
Pressure Control

The Waterous Discharge Relief Valve system provides sensitive pump control to protect firefighters from sudden pressure surges resulting from changes in discharge flows from the pump.  Designed with a ‘‘built–in–memory’’, this system has a wide continuous range of pressure control from a minimum of 75 to a maximum of 300 psig (5.2 to 20.7 bar) depending upon pump performance characteristics, and may be put in or taken out of operation without disturbing the pressure setting. This lets you leave the system at a pre–set ‘‘ready–to–use’’ pressure setting.

The Waterous discharge relief valve system incorporates two separate units, a panel mounted pilot valve which controls the operation of the relief valve proper, and the relief valve which is normally mounted on the pump.

The pilot valve has two controls, one to adjust the relief valve operating pressure, and the other, an ON-OFF control, to place the relief valve in or out of operation.

The ON-OFF control lets the operator put the relief valve out of operation (hydraulically holding the relief valve closed) when a pressure higher than set pressure or higher than 300 psig (20.7 bar) is desired. Turning this control ON permits the relief valve to operate again at whatever pressure was previously set without further adjustment.

The relief valve is mounted on the pump or in the piping between the intake and discharge sides of the pump. It modulates flow between discharge and intake by ranging between the fully open and fully closed position in response to hydraulic signals from the pilot valve. The relief valve is available in three sizes. A two-inch diameter relief valve is used on pumps with rated capacities of 750 GPM (2850 L/min.) or less. For pumps with rated capacities through 1250 GPM (4750 L/min.), a three-inch diameter relief valve is used. For pumps with rated capacities of 1250 GPM through 2000 GPM (4750 through 7800 L/min.), a four-inch relief valve is used.

Among the features that make the Waterous discharge relief valve system reliable and simple to use and maintain are:

- Corrosion resistant brass, bronze and stainless steel used in all critical areas throughout the system.

- An easily cleaned pilot valve strainer that can be removed from the panel and cleaned even while the pump is operating.

- A smooth-turning pressure control with exclusive needle thrust bearing for precise pressure control adjustment.

- No diaphragm to become strained or ruptured.

- An easily removeable orifice that permits quick and simple cleaning or replacement.

- Two indicator lights show the position of the relief valve; green for fully closed and amber for at least partially open.

The discharge relief valve replacement kit is available for installation on almost any type of fire pump. Kits come complete with 2 inch, 2-1/2 inch or 3 inch NPT tapped flanges, gaskets and flange mounting hardware. You furnish the pipe and install between intake and discharge.

When you purchase Waterous equipment, not only do you get quality products, you get quality service. Our expert service technicians are the best in the business and they are always happy to answer any service questions you might have.

Sales/Applications Assistance	Service Assistance
Phone: 651-450-5234 (Press 3) 	Phone: 651-450-5200
pumps@waterousco.com 	Fax: 800-488-1228

service@waterousco.com

SPECIFICATIONS - accessories: Discharge relief valve

Installation:

Select an opening on your pump intake and discharge, preferably  at the two closest points to minimize friction loss, and install the relief valve. The pilot valve requires three lengths of 3/8 inch copper tubing which will extend from pump discharge to the pilot valve, from the pilot valve to relief valve, and from the pilot valve to pump intake.

3” Relief Valve:

For capacities through 1250 GPM (4750 L/min). Shown mounted between discharge and intake on a standard Waterous midship mounted pump.

Schematic Showing Relief Valve Operation

# Text boxes

Description:

Industry-Leading Sales and Support

Discharge Relief Valve Replacement Kit:

PILOT VALVE:

Mounted on the pump control panel. Hydraulically controls the operation of the relief valve.

Special Features: