SPECIFICATIONS – Slide-in cafsystems: 150-70-DS
Modular Slide-In CAFSystems™ Designed For Easy Operation

The 150−70−DS is a slide−in modular compressed air foam unit designed and constructed to discharge water, foam solution or compressed air foam. The consistency of the compressed air foam from each discharge is individually adjustable.

| 150-70-DS Performance |
| --- |
|  | FLOW | PRESSURE |
|  | GPM | l/min | l/sec | PSI | bar | kPa | MPa |
| Water Flow | 150 | 600 | 10 | 150 | 10 | 1000 | 1.0 |
|  | CFM | M3/Min | PSI | Bar | kPa | MPa |
| Air Flow | 70 | 2.0 | 100 | 7 | 700 | 0.7 |

Pump and Transmission Specifications

SPECIFICATIONS – Slide-in cafsystems: 150-70-DS

Air Compressor:

The air compressor is an oil-flooded, rotary screw type, sized to supply a minimum of 70 scfm (1.98 m3/min) of usable air.

Pneumatic Modulating Inlet Valve:

The air compressor is controlled by the pneumatic modulation inlet valve mounted on the air end. The pneumatic modulation inlet valve controls air delivery while maintaining constant pressure.

Auto Sync Balancing System:

Automatically maintains the air pressure within +/- 5% of the water pump pressure throughout the pressure range. The Auto Sync Balancing System is located on the operator's panel and allows for the following modes:

- Automatic - Air pressure matched to water pressure

- Fixed - Air pressure defaults to manual setting on compressor mounted control valve.

- Unload - Air pressure reduced to 40 psig (2.8 bar) for standby operations

Air Compressor Oil System:

A spin-on, full-flow oil filter unit is part of the system to control oil flow to the cooler. All lines are routed in braided hose conforming to SAE 100R1 standards for hydraulic hose.

Modular Air/Oil Separator:

Replacement elements for the oil filter and separator are available.

Air Compressor Cooling System:

The air compressor is cooled by the unit's water pump, utilizing a copper and brass shell and tube heat exchanger. When the fire pump is operating, water flows through the heat exchanger. The system maintains recommended operating temperatures throughout the full operational range in ambient temperatures up to 115°F (46.1° C).

Air Lines:

All air lines are rated to a minimum of 250 psig (17.2 bar). Air line fittings are constructed of brass, bronze or steel. Stainless steel or brass check valves are provided at all air injection points to prevent water back-flow into the air lines. All hoses shall be secured to the frame with insulating clamps and located away from any heat sources.

Plumbing:

Inlet:

Inlet piping is 2” stainless steel pipe.

Discharge:

Plumbing to two panel mounted 1-1/2” discharge outlets incorporate a stainless steel manifold and welded stainless steel pipe. All discharge plumbing is designed and tested to a minimum of 500 psig (34.5 bar) burst pressure.

Drains:

Panel mounted drain valves are provided to drain water from the water pump, discharge manifold and compressor cooler.

Foam Proportioner:

Aquis™ Foam Proportioner with operator interface terminal (OIT), pump module with electric motor/motor driver and microcontroller unit, foam concentrate strainer, shielded electrical cables for connection of all electronic components, foam inject check valve, WYE Strainer and flowmeter and tee.

On-Site Delivery Instruction (Optional):

Contact factory for pricing.

# Text boxes

- Waterous  CPD-2 Centrifugal water pump utilizing close-grained iron case, reinforced nylon impeller, stainless steel shaft and maintenance-free mechanical seal.

- 2- inch Intake

- 1-1/2 inch Discharge

- Pneumatic oil-free primer capable of priming the water pump through 20 feet (6 m) of 2-1/2 (63.5 mm) inch hard intake hose with a 10 foot (3 m) lift. Controls are mounted on the operator's panel.

- “Poly Chain” drive transmission with an automatic tensioner and 8mm pitch sprockets.

Engine Specifications

- Deutz, Model 4FM2011, three-cylinder, turbocharged, air/oil-cooled, delivering a maximum of 48 HP (35.8 kW), four-cycle, diesel fueled.Two (2) year manufacturer's warranty.

- The engine draws fuel from a fuel tank (not supplied) via a pulse fuel pump.

- Pressure lube system with spin-on oil filter. An extension hose is installed on the engine oil drain with a valve located at the oil pan and a plug installed in the end of the hose to facilitate oil changes.

- 12-volt electric with 60A alternator, electric ignition and start switch.

- Heavy Duty Exhaust Muffler

Frame:

High-strength, welded tubular steel frame provided to support and contain the entire CAFS unit. Constructed of 1-1/4” tubing with radius corners and a durable corrosion-resistant powder coat finish.

Pump Operator's Panel:

- 3-position compressor control switch

- Water and air pressure gauges

- Air compressor temperature warning light and alarm

- Engine oil pressure warning light and alarm

- Engine temperature warning light and alarm

- Engine ignition and start switch

- Compressor Auto Sync control panel w/instruction plate

- Proportioner control w/instruction plate

- Chrome-plated discharge connection

- Priming system controls w/instruction plate

- Auxiliary compressed air outlet and valve control

- Removable engine access panel w/flow schematic

Foam Proportioner

Aquis™ Foam Proportioner

Warranty

Waterous Five-Year Limited Warranty

Conditions of Sales

For details on Waterous Conditions of Sales, refer to F-2190, Conditions of Sales located on the Waterous web site at www.waterousco.com or by contacting Waterous.

Industry Leading Sales and Support

When you purchase equipment, not only do you get quality products, you get quality service. Our expert service technicians are the best in the business and they are always happy to answer any service questions you might have.

Sales/Applications Assistance	Service Assistance
Phone: 651-450-5234 (Press 3) 	Phone: 651-450-5200
pumpsales@waterousco.com 	Fax: 800-488-1228

service@waterousco.com

RAISING THE BAR ON INNOVATION, RELIABILITY AND SERVICE.